## Registers
synapsus – Modbus TCP registers (BMS)
Signed 16-bit integers; scale x10: value read / 10; 32767 = no sensor, fault or not applicable. Access W (yellow background): writable if BMS commands are allowed on the tablet.
Address | Area | Name | Scale | Unit | Access | Note
0 | System | Serial number, high word | 1 |  | R | number = register 0 x 65536 + register 1 (unsigned)
1 | System | Serial number, low word | 1 |  | R
2 | System | Application version (code) | 1 |  | R
3 | System | Life counter | 1 | s | R | +1 per second, restarts at 0 after 32766; frozen = tablet frozen
4 | System | Outdoor temperature | x10 | °C | R
5 | System | Modbus bus of the modules | 1 |  | R | 0 ok, 1 partial, 2 down
6 | System | Sensor fault in progress | 1 |  | R | 0 / 1
7 | System | Number of active alarms | 1 |  | R
100 | Heat pump | Heat pump: phase | 1 |  | R | 0 stopped, 1 start requested, 2 to 4 starting up, 5 running, 10 stop requested, 99 blocked
101 | Heat pump | Heat pump: enabled | 1 |  | R/W | 0 / 1
102 | Heat pump | Heat pump: blocked | 1 |  | R | 0 / 1
103 | Heat pump | Heat pump: compressor running | 1 |  | R | 0 / 1
104 | Heat pump | Heat pump: mode | 1 |  | R | 0 none, 1 heating, 2 cooling
105 | Heat pump | Compressor speed | 1 | % | R | 32767 without a drive
106 | Heat pump | Evaporator speed | 1 | % | R
107 | Heat pump | Condenser speed | 1 | % | R
108 | Heat pump | Low pressure | x10 | bar | R
109 | Heat pump | High pressure | x10 | bar | R
110 | Heat pump | Evaporation temperature | x10 | °C | R
111 | Heat pump | Condensation temperature | x10 | °C | R
112 | Heat pump | Superheat | x10 | °C | R
113 | Heat pump | Subcooling | x10 | °C | R
114 | Heat pump | E1 Condenser inlet | x10 | °C | R
115 | Heat pump | E2 Condenser outlet | x10 | °C | R
116 | Heat pump | E3 Evaporator inlet | x10 | °C | R
117 | Heat pump | E4 Evaporator outlet | x10 | °C | R
118 | Heat pump | E5 Evaporator | x10 | °C | R
119 | Heat pump | Evaporator flow | x10 | l/min | R
120 | Heat pump | Condenser flow | x10 | l/min | R
121 | Heat pump | Expansion valve position | 1 | steps | R | 0 to 480
122 | Heat pump | Drive frequency | x10 | Hz | R
123 | Heat pump | Drive power | x100 | kW | R
130 | Heat pump | Command: unblock the heat pump | 1 |  | W | write 1; reads 0
131 | Heat pump | Heat pump group: role | 1 |  | R | 1 stand-alone, 2 master, 3 slave
132 | Heat pump | Heat pump group: link | 1 |  | R | master: number of slaves online; slave: master reachable 0 / 1; stand-alone: 0
133 | Heat pump | Heat pump group: quiet mode imposed | 1 |  | R | 0 / 1
134 | Heat pump | Heat pump group: group functions in progress | 1 |  | R | master: functions where a heat pump is working; slave: group functions served
200 | Alarms | Alarm 0: LP threshold | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
201 | Alarms | Alarm 1: HP threshold | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
202 | Alarms | Alarm 2: Min. evap. flow | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
203 | Alarms | Alarm 3: Min. cond. flow | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
204 | Alarms | Alarm 4: Max. temperature | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
205 | Alarms | Alarm 5: Total Modbus failure | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
206 | Alarms | Alarm 6: Low evaporator water pressure | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
207 | Alarms | Alarm 7: Low condenser water pressure | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
208 | Alarms | Alarm 8: Evaporator water pressure lockout | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
209 | Alarms | Alarm 9: Condenser water pressure lockout | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
210 | Alarms | Alarm 10: Evaporator safety | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
211 | Alarms | Alarm 11: Condenser safety | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
212 | Alarms | Alarm 12: Compressor drive fault | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
213 | Alarms | Alarm 13: Compressor drive communication | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
214 | Alarms | Alarm 14: Compressor not started | 1 |  | R | 0 none, 1 being confirmed, 3 confirmed
250 | Alarms | Active alarms, as bits | 1 |  | R | bit n = alarm n
1000 | Functions: Hot room | Hot room no. 1: present | 1 |  | R | 0 / 1
1001 | Functions: Hot room | Hot room no. 1: enabled | 1 |  | R/W | 0 / 1
1002 | Functions: Hot room | Hot room no. 1: running | 1 |  | R | 0 / 1
1003 | Functions: Hot room | Hot room no. 1: temperature | x10 | °C | R
1004 | Functions: Hot room | Hot room no. 1: current setpoint | x10 | °C | R
1005 | Functions: Hot room | Hot room no. 1: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1006 | Functions: Hot room | Hot room no. 1: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1007 | Functions: Hot room | Hot room no. 1: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1010 | Functions: Hot room | Hot room no. 2: present | 1 |  | R | 0 / 1
1011 | Functions: Hot room | Hot room no. 2: enabled | 1 |  | R/W | 0 / 1
1012 | Functions: Hot room | Hot room no. 2: running | 1 |  | R | 0 / 1
1013 | Functions: Hot room | Hot room no. 2: temperature | x10 | °C | R
1014 | Functions: Hot room | Hot room no. 2: current setpoint | x10 | °C | R
1015 | Functions: Hot room | Hot room no. 2: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1016 | Functions: Hot room | Hot room no. 2: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1017 | Functions: Hot room | Hot room no. 2: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1020 | Functions: Hot room | Hot room no. 3: present | 1 |  | R | 0 / 1
1021 | Functions: Hot room | Hot room no. 3: enabled | 1 |  | R/W | 0 / 1
1022 | Functions: Hot room | Hot room no. 3: running | 1 |  | R | 0 / 1
1023 | Functions: Hot room | Hot room no. 3: temperature | x10 | °C | R
1024 | Functions: Hot room | Hot room no. 3: current setpoint | x10 | °C | R
1025 | Functions: Hot room | Hot room no. 3: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1026 | Functions: Hot room | Hot room no. 3: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1027 | Functions: Hot room | Hot room no. 3: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1030 | Functions: Hot room | Hot room no. 4: present | 1 |  | R | 0 / 1
1031 | Functions: Hot room | Hot room no. 4: enabled | 1 |  | R/W | 0 / 1
1032 | Functions: Hot room | Hot room no. 4: running | 1 |  | R | 0 / 1
1033 | Functions: Hot room | Hot room no. 4: temperature | x10 | °C | R
1034 | Functions: Hot room | Hot room no. 4: current setpoint | x10 | °C | R
1035 | Functions: Hot room | Hot room no. 4: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1036 | Functions: Hot room | Hot room no. 4: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1037 | Functions: Hot room | Hot room no. 4: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1040 | Functions: Hot room | Hot room no. 5: present | 1 |  | R | 0 / 1
1041 | Functions: Hot room | Hot room no. 5: enabled | 1 |  | R/W | 0 / 1
1042 | Functions: Hot room | Hot room no. 5: running | 1 |  | R | 0 / 1
1043 | Functions: Hot room | Hot room no. 5: temperature | x10 | °C | R
1044 | Functions: Hot room | Hot room no. 5: current setpoint | x10 | °C | R
1045 | Functions: Hot room | Hot room no. 5: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1046 | Functions: Hot room | Hot room no. 5: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1047 | Functions: Hot room | Hot room no. 5: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1050 | Functions: Hot room | Hot room no. 6: present | 1 |  | R | 0 / 1
1051 | Functions: Hot room | Hot room no. 6: enabled | 1 |  | R/W | 0 / 1
1052 | Functions: Hot room | Hot room no. 6: running | 1 |  | R | 0 / 1
1053 | Functions: Hot room | Hot room no. 6: temperature | x10 | °C | R
1054 | Functions: Hot room | Hot room no. 6: current setpoint | x10 | °C | R
1055 | Functions: Hot room | Hot room no. 6: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1056 | Functions: Hot room | Hot room no. 6: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1057 | Functions: Hot room | Hot room no. 6: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1060 | Functions: Hot room | Hot room no. 7: present | 1 |  | R | 0 / 1
1061 | Functions: Hot room | Hot room no. 7: enabled | 1 |  | R/W | 0 / 1
1062 | Functions: Hot room | Hot room no. 7: running | 1 |  | R | 0 / 1
1063 | Functions: Hot room | Hot room no. 7: temperature | x10 | °C | R
1064 | Functions: Hot room | Hot room no. 7: current setpoint | x10 | °C | R
1065 | Functions: Hot room | Hot room no. 7: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1066 | Functions: Hot room | Hot room no. 7: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1067 | Functions: Hot room | Hot room no. 7: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1070 | Functions: Hot room | Hot room no. 8: present | 1 |  | R | 0 / 1
1071 | Functions: Hot room | Hot room no. 8: enabled | 1 |  | R/W | 0 / 1
1072 | Functions: Hot room | Hot room no. 8: running | 1 |  | R | 0 / 1
1073 | Functions: Hot room | Hot room no. 8: temperature | x10 | °C | R
1074 | Functions: Hot room | Hot room no. 8: current setpoint | x10 | °C | R
1075 | Functions: Hot room | Hot room no. 8: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1076 | Functions: Hot room | Hot room no. 8: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1077 | Functions: Hot room | Hot room no. 8: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1080 | Functions: Hot room | Hot room no. 9: present | 1 |  | R | 0 / 1
1081 | Functions: Hot room | Hot room no. 9: enabled | 1 |  | R/W | 0 / 1
1082 | Functions: Hot room | Hot room no. 9: running | 1 |  | R | 0 / 1
1083 | Functions: Hot room | Hot room no. 9: temperature | x10 | °C | R
1084 | Functions: Hot room | Hot room no. 9: current setpoint | x10 | °C | R
1085 | Functions: Hot room | Hot room no. 9: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1086 | Functions: Hot room | Hot room no. 9: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1087 | Functions: Hot room | Hot room no. 9: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1090 | Functions: Hot room | Hot room no. 10: present | 1 |  | R | 0 / 1
1091 | Functions: Hot room | Hot room no. 10: enabled | 1 |  | R/W | 0 / 1
1092 | Functions: Hot room | Hot room no. 10: running | 1 |  | R | 0 / 1
1093 | Functions: Hot room | Hot room no. 10: temperature | x10 | °C | R
1094 | Functions: Hot room | Hot room no. 10: current setpoint | x10 | °C | R
1095 | Functions: Hot room | Hot room no. 10: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1096 | Functions: Hot room | Hot room no. 10: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1097 | Functions: Hot room | Hot room no. 10: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1100 | Functions: Cold room | Cold room no. 1: present | 1 |  | R | 0 / 1
1101 | Functions: Cold room | Cold room no. 1: enabled | 1 |  | R/W | 0 / 1
1102 | Functions: Cold room | Cold room no. 1: running | 1 |  | R | 0 / 1
1103 | Functions: Cold room | Cold room no. 1: temperature | x10 | °C | R
1104 | Functions: Cold room | Cold room no. 1: current setpoint | x10 | °C | R
1105 | Functions: Cold room | Cold room no. 1: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1106 | Functions: Cold room | Cold room no. 1: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1107 | Functions: Cold room | Cold room no. 1: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1110 | Functions: Cold room | Cold room no. 2: present | 1 |  | R | 0 / 1
1111 | Functions: Cold room | Cold room no. 2: enabled | 1 |  | R/W | 0 / 1
1112 | Functions: Cold room | Cold room no. 2: running | 1 |  | R | 0 / 1
1113 | Functions: Cold room | Cold room no. 2: temperature | x10 | °C | R
1114 | Functions: Cold room | Cold room no. 2: current setpoint | x10 | °C | R
1115 | Functions: Cold room | Cold room no. 2: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1116 | Functions: Cold room | Cold room no. 2: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1117 | Functions: Cold room | Cold room no. 2: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1120 | Functions: Cold room | Cold room no. 3: present | 1 |  | R | 0 / 1
1121 | Functions: Cold room | Cold room no. 3: enabled | 1 |  | R/W | 0 / 1
1122 | Functions: Cold room | Cold room no. 3: running | 1 |  | R | 0 / 1
1123 | Functions: Cold room | Cold room no. 3: temperature | x10 | °C | R
1124 | Functions: Cold room | Cold room no. 3: current setpoint | x10 | °C | R
1125 | Functions: Cold room | Cold room no. 3: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1126 | Functions: Cold room | Cold room no. 3: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1127 | Functions: Cold room | Cold room no. 3: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1130 | Functions: Cold room | Cold room no. 4: present | 1 |  | R | 0 / 1
1131 | Functions: Cold room | Cold room no. 4: enabled | 1 |  | R/W | 0 / 1
1132 | Functions: Cold room | Cold room no. 4: running | 1 |  | R | 0 / 1
1133 | Functions: Cold room | Cold room no. 4: temperature | x10 | °C | R
1134 | Functions: Cold room | Cold room no. 4: current setpoint | x10 | °C | R
1135 | Functions: Cold room | Cold room no. 4: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1136 | Functions: Cold room | Cold room no. 4: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1137 | Functions: Cold room | Cold room no. 4: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1140 | Functions: Cold room | Cold room no. 5: present | 1 |  | R | 0 / 1
1141 | Functions: Cold room | Cold room no. 5: enabled | 1 |  | R/W | 0 / 1
1142 | Functions: Cold room | Cold room no. 5: running | 1 |  | R | 0 / 1
1143 | Functions: Cold room | Cold room no. 5: temperature | x10 | °C | R
1144 | Functions: Cold room | Cold room no. 5: current setpoint | x10 | °C | R
1145 | Functions: Cold room | Cold room no. 5: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1146 | Functions: Cold room | Cold room no. 5: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1147 | Functions: Cold room | Cold room no. 5: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1150 | Functions: Cold room | Cold room no. 6: present | 1 |  | R | 0 / 1
1151 | Functions: Cold room | Cold room no. 6: enabled | 1 |  | R/W | 0 / 1
1152 | Functions: Cold room | Cold room no. 6: running | 1 |  | R | 0 / 1
1153 | Functions: Cold room | Cold room no. 6: temperature | x10 | °C | R
1154 | Functions: Cold room | Cold room no. 6: current setpoint | x10 | °C | R
1155 | Functions: Cold room | Cold room no. 6: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1156 | Functions: Cold room | Cold room no. 6: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1157 | Functions: Cold room | Cold room no. 6: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1160 | Functions: Cold room | Cold room no. 7: present | 1 |  | R | 0 / 1
1161 | Functions: Cold room | Cold room no. 7: enabled | 1 |  | R/W | 0 / 1
1162 | Functions: Cold room | Cold room no. 7: running | 1 |  | R | 0 / 1
1163 | Functions: Cold room | Cold room no. 7: temperature | x10 | °C | R
1164 | Functions: Cold room | Cold room no. 7: current setpoint | x10 | °C | R
1165 | Functions: Cold room | Cold room no. 7: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1166 | Functions: Cold room | Cold room no. 7: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1167 | Functions: Cold room | Cold room no. 7: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1170 | Functions: Cold room | Cold room no. 8: present | 1 |  | R | 0 / 1
1171 | Functions: Cold room | Cold room no. 8: enabled | 1 |  | R/W | 0 / 1
1172 | Functions: Cold room | Cold room no. 8: running | 1 |  | R | 0 / 1
1173 | Functions: Cold room | Cold room no. 8: temperature | x10 | °C | R
1174 | Functions: Cold room | Cold room no. 8: current setpoint | x10 | °C | R
1175 | Functions: Cold room | Cold room no. 8: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1176 | Functions: Cold room | Cold room no. 8: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1177 | Functions: Cold room | Cold room no. 8: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1180 | Functions: Cold room | Cold room no. 9: present | 1 |  | R | 0 / 1
1181 | Functions: Cold room | Cold room no. 9: enabled | 1 |  | R/W | 0 / 1
1182 | Functions: Cold room | Cold room no. 9: running | 1 |  | R | 0 / 1
1183 | Functions: Cold room | Cold room no. 9: temperature | x10 | °C | R
1184 | Functions: Cold room | Cold room no. 9: current setpoint | x10 | °C | R
1185 | Functions: Cold room | Cold room no. 9: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1186 | Functions: Cold room | Cold room no. 9: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1187 | Functions: Cold room | Cold room no. 9: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1190 | Functions: Cold room | Cold room no. 10: present | 1 |  | R | 0 / 1
1191 | Functions: Cold room | Cold room no. 10: enabled | 1 |  | R/W | 0 / 1
1192 | Functions: Cold room | Cold room no. 10: running | 1 |  | R | 0 / 1
1193 | Functions: Cold room | Cold room no. 10: temperature | x10 | °C | R
1194 | Functions: Cold room | Cold room no. 10: current setpoint | x10 | °C | R
1195 | Functions: Cold room | Cold room no. 10: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1196 | Functions: Cold room | Cold room no. 10: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1197 | Functions: Cold room | Cold room no. 10: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1200 | Functions: Hot tank | Hot tank no. 1: present | 1 |  | R | 0 / 1
1201 | Functions: Hot tank | Hot tank no. 1: enabled | 1 |  | R/W | 0 / 1
1202 | Functions: Hot tank | Hot tank no. 1: running | 1 |  | R | 0 / 1
1203 | Functions: Hot tank | Hot tank no. 1: temperature | x10 | °C | R
1204 | Functions: Hot tank | Hot tank no. 1: current setpoint | x10 | °C | R
1205 | Functions: Hot tank | Hot tank no. 1: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1206 | Functions: Hot tank | Hot tank no. 1: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1207 | Functions: Hot tank | Hot tank no. 1: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1210 | Functions: Hot tank | Hot tank no. 2: present | 1 |  | R | 0 / 1
1211 | Functions: Hot tank | Hot tank no. 2: enabled | 1 |  | R/W | 0 / 1
1212 | Functions: Hot tank | Hot tank no. 2: running | 1 |  | R | 0 / 1
1213 | Functions: Hot tank | Hot tank no. 2: temperature | x10 | °C | R
1214 | Functions: Hot tank | Hot tank no. 2: current setpoint | x10 | °C | R
1215 | Functions: Hot tank | Hot tank no. 2: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1216 | Functions: Hot tank | Hot tank no. 2: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1217 | Functions: Hot tank | Hot tank no. 2: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1220 | Functions: Hot tank | Hot tank no. 3: present | 1 |  | R | 0 / 1
1221 | Functions: Hot tank | Hot tank no. 3: enabled | 1 |  | R/W | 0 / 1
1222 | Functions: Hot tank | Hot tank no. 3: running | 1 |  | R | 0 / 1
1223 | Functions: Hot tank | Hot tank no. 3: temperature | x10 | °C | R
1224 | Functions: Hot tank | Hot tank no. 3: current setpoint | x10 | °C | R
1225 | Functions: Hot tank | Hot tank no. 3: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1226 | Functions: Hot tank | Hot tank no. 3: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1227 | Functions: Hot tank | Hot tank no. 3: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1230 | Functions: Hot tank | Hot tank no. 4: present | 1 |  | R | 0 / 1
1231 | Functions: Hot tank | Hot tank no. 4: enabled | 1 |  | R/W | 0 / 1
1232 | Functions: Hot tank | Hot tank no. 4: running | 1 |  | R | 0 / 1
1233 | Functions: Hot tank | Hot tank no. 4: temperature | x10 | °C | R
1234 | Functions: Hot tank | Hot tank no. 4: current setpoint | x10 | °C | R
1235 | Functions: Hot tank | Hot tank no. 4: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1236 | Functions: Hot tank | Hot tank no. 4: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1237 | Functions: Hot tank | Hot tank no. 4: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1240 | Functions: Hot tank | Hot tank no. 5: present | 1 |  | R | 0 / 1
1241 | Functions: Hot tank | Hot tank no. 5: enabled | 1 |  | R/W | 0 / 1
1242 | Functions: Hot tank | Hot tank no. 5: running | 1 |  | R | 0 / 1
1243 | Functions: Hot tank | Hot tank no. 5: temperature | x10 | °C | R
1244 | Functions: Hot tank | Hot tank no. 5: current setpoint | x10 | °C | R
1245 | Functions: Hot tank | Hot tank no. 5: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1246 | Functions: Hot tank | Hot tank no. 5: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1247 | Functions: Hot tank | Hot tank no. 5: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1250 | Functions: Hot tank | Hot tank no. 6: present | 1 |  | R | 0 / 1
1251 | Functions: Hot tank | Hot tank no. 6: enabled | 1 |  | R/W | 0 / 1
1252 | Functions: Hot tank | Hot tank no. 6: running | 1 |  | R | 0 / 1
1253 | Functions: Hot tank | Hot tank no. 6: temperature | x10 | °C | R
1254 | Functions: Hot tank | Hot tank no. 6: current setpoint | x10 | °C | R
1255 | Functions: Hot tank | Hot tank no. 6: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1256 | Functions: Hot tank | Hot tank no. 6: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1257 | Functions: Hot tank | Hot tank no. 6: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1260 | Functions: Hot tank | Hot tank no. 7: present | 1 |  | R | 0 / 1
1261 | Functions: Hot tank | Hot tank no. 7: enabled | 1 |  | R/W | 0 / 1
1262 | Functions: Hot tank | Hot tank no. 7: running | 1 |  | R | 0 / 1
1263 | Functions: Hot tank | Hot tank no. 7: temperature | x10 | °C | R
1264 | Functions: Hot tank | Hot tank no. 7: current setpoint | x10 | °C | R
1265 | Functions: Hot tank | Hot tank no. 7: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1266 | Functions: Hot tank | Hot tank no. 7: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1267 | Functions: Hot tank | Hot tank no. 7: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1270 | Functions: Hot tank | Hot tank no. 8: present | 1 |  | R | 0 / 1
1271 | Functions: Hot tank | Hot tank no. 8: enabled | 1 |  | R/W | 0 / 1
1272 | Functions: Hot tank | Hot tank no. 8: running | 1 |  | R | 0 / 1
1273 | Functions: Hot tank | Hot tank no. 8: temperature | x10 | °C | R
1274 | Functions: Hot tank | Hot tank no. 8: current setpoint | x10 | °C | R
1275 | Functions: Hot tank | Hot tank no. 8: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1276 | Functions: Hot tank | Hot tank no. 8: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1277 | Functions: Hot tank | Hot tank no. 8: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1280 | Functions: Hot tank | Hot tank no. 9: present | 1 |  | R | 0 / 1
1281 | Functions: Hot tank | Hot tank no. 9: enabled | 1 |  | R/W | 0 / 1
1282 | Functions: Hot tank | Hot tank no. 9: running | 1 |  | R | 0 / 1
1283 | Functions: Hot tank | Hot tank no. 9: temperature | x10 | °C | R
1284 | Functions: Hot tank | Hot tank no. 9: current setpoint | x10 | °C | R
1285 | Functions: Hot tank | Hot tank no. 9: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1286 | Functions: Hot tank | Hot tank no. 9: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1287 | Functions: Hot tank | Hot tank no. 9: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1290 | Functions: Hot tank | Hot tank no. 10: present | 1 |  | R | 0 / 1
1291 | Functions: Hot tank | Hot tank no. 10: enabled | 1 |  | R/W | 0 / 1
1292 | Functions: Hot tank | Hot tank no. 10: running | 1 |  | R | 0 / 1
1293 | Functions: Hot tank | Hot tank no. 10: temperature | x10 | °C | R
1294 | Functions: Hot tank | Hot tank no. 10: current setpoint | x10 | °C | R
1295 | Functions: Hot tank | Hot tank no. 10: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1296 | Functions: Hot tank | Hot tank no. 10: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1297 | Functions: Hot tank | Hot tank no. 10: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1300 | Functions: Cold tank | Cold tank no. 1: present | 1 |  | R | 0 / 1
1301 | Functions: Cold tank | Cold tank no. 1: enabled | 1 |  | R/W | 0 / 1
1302 | Functions: Cold tank | Cold tank no. 1: running | 1 |  | R | 0 / 1
1303 | Functions: Cold tank | Cold tank no. 1: temperature | x10 | °C | R
1304 | Functions: Cold tank | Cold tank no. 1: current setpoint | x10 | °C | R
1305 | Functions: Cold tank | Cold tank no. 1: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1306 | Functions: Cold tank | Cold tank no. 1: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1307 | Functions: Cold tank | Cold tank no. 1: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1310 | Functions: Cold tank | Cold tank no. 2: present | 1 |  | R | 0 / 1
1311 | Functions: Cold tank | Cold tank no. 2: enabled | 1 |  | R/W | 0 / 1
1312 | Functions: Cold tank | Cold tank no. 2: running | 1 |  | R | 0 / 1
1313 | Functions: Cold tank | Cold tank no. 2: temperature | x10 | °C | R
1314 | Functions: Cold tank | Cold tank no. 2: current setpoint | x10 | °C | R
1315 | Functions: Cold tank | Cold tank no. 2: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1316 | Functions: Cold tank | Cold tank no. 2: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1317 | Functions: Cold tank | Cold tank no. 2: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1320 | Functions: Cold tank | Cold tank no. 3: present | 1 |  | R | 0 / 1
1321 | Functions: Cold tank | Cold tank no. 3: enabled | 1 |  | R/W | 0 / 1
1322 | Functions: Cold tank | Cold tank no. 3: running | 1 |  | R | 0 / 1
1323 | Functions: Cold tank | Cold tank no. 3: temperature | x10 | °C | R
1324 | Functions: Cold tank | Cold tank no. 3: current setpoint | x10 | °C | R
1325 | Functions: Cold tank | Cold tank no. 3: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1326 | Functions: Cold tank | Cold tank no. 3: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1327 | Functions: Cold tank | Cold tank no. 3: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1330 | Functions: Cold tank | Cold tank no. 4: present | 1 |  | R | 0 / 1
1331 | Functions: Cold tank | Cold tank no. 4: enabled | 1 |  | R/W | 0 / 1
1332 | Functions: Cold tank | Cold tank no. 4: running | 1 |  | R | 0 / 1
1333 | Functions: Cold tank | Cold tank no. 4: temperature | x10 | °C | R
1334 | Functions: Cold tank | Cold tank no. 4: current setpoint | x10 | °C | R
1335 | Functions: Cold tank | Cold tank no. 4: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1336 | Functions: Cold tank | Cold tank no. 4: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1337 | Functions: Cold tank | Cold tank no. 4: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1340 | Functions: Cold tank | Cold tank no. 5: present | 1 |  | R | 0 / 1
1341 | Functions: Cold tank | Cold tank no. 5: enabled | 1 |  | R/W | 0 / 1
1342 | Functions: Cold tank | Cold tank no. 5: running | 1 |  | R | 0 / 1
1343 | Functions: Cold tank | Cold tank no. 5: temperature | x10 | °C | R
1344 | Functions: Cold tank | Cold tank no. 5: current setpoint | x10 | °C | R
1345 | Functions: Cold tank | Cold tank no. 5: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1346 | Functions: Cold tank | Cold tank no. 5: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1347 | Functions: Cold tank | Cold tank no. 5: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1350 | Functions: Cold tank | Cold tank no. 6: present | 1 |  | R | 0 / 1
1351 | Functions: Cold tank | Cold tank no. 6: enabled | 1 |  | R/W | 0 / 1
1352 | Functions: Cold tank | Cold tank no. 6: running | 1 |  | R | 0 / 1
1353 | Functions: Cold tank | Cold tank no. 6: temperature | x10 | °C | R
1354 | Functions: Cold tank | Cold tank no. 6: current setpoint | x10 | °C | R
1355 | Functions: Cold tank | Cold tank no. 6: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1356 | Functions: Cold tank | Cold tank no. 6: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1357 | Functions: Cold tank | Cold tank no. 6: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1360 | Functions: Cold tank | Cold tank no. 7: present | 1 |  | R | 0 / 1
1361 | Functions: Cold tank | Cold tank no. 7: enabled | 1 |  | R/W | 0 / 1
1362 | Functions: Cold tank | Cold tank no. 7: running | 1 |  | R | 0 / 1
1363 | Functions: Cold tank | Cold tank no. 7: temperature | x10 | °C | R
1364 | Functions: Cold tank | Cold tank no. 7: current setpoint | x10 | °C | R
1365 | Functions: Cold tank | Cold tank no. 7: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1366 | Functions: Cold tank | Cold tank no. 7: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1367 | Functions: Cold tank | Cold tank no. 7: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1370 | Functions: Cold tank | Cold tank no. 8: present | 1 |  | R | 0 / 1
1371 | Functions: Cold tank | Cold tank no. 8: enabled | 1 |  | R/W | 0 / 1
1372 | Functions: Cold tank | Cold tank no. 8: running | 1 |  | R | 0 / 1
1373 | Functions: Cold tank | Cold tank no. 8: temperature | x10 | °C | R
1374 | Functions: Cold tank | Cold tank no. 8: current setpoint | x10 | °C | R
1375 | Functions: Cold tank | Cold tank no. 8: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1376 | Functions: Cold tank | Cold tank no. 8: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1377 | Functions: Cold tank | Cold tank no. 8: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1380 | Functions: Cold tank | Cold tank no. 9: present | 1 |  | R | 0 / 1
1381 | Functions: Cold tank | Cold tank no. 9: enabled | 1 |  | R/W | 0 / 1
1382 | Functions: Cold tank | Cold tank no. 9: running | 1 |  | R | 0 / 1
1383 | Functions: Cold tank | Cold tank no. 9: temperature | x10 | °C | R
1384 | Functions: Cold tank | Cold tank no. 9: current setpoint | x10 | °C | R
1385 | Functions: Cold tank | Cold tank no. 9: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1386 | Functions: Cold tank | Cold tank no. 9: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1387 | Functions: Cold tank | Cold tank no. 9: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1390 | Functions: Cold tank | Cold tank no. 10: present | 1 |  | R | 0 / 1
1391 | Functions: Cold tank | Cold tank no. 10: enabled | 1 |  | R/W | 0 / 1
1392 | Functions: Cold tank | Cold tank no. 10: running | 1 |  | R | 0 / 1
1393 | Functions: Cold tank | Cold tank no. 10: temperature | x10 | °C | R
1394 | Functions: Cold tank | Cold tank no. 10: current setpoint | x10 | °C | R
1395 | Functions: Cold tank | Cold tank no. 10: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1396 | Functions: Cold tank | Cold tank no. 10: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1397 | Functions: Cold tank | Cold tank no. 10: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1400 | Functions: Hot water | Hot water no. 1: present | 1 |  | R | 0 / 1
1401 | Functions: Hot water | Hot water no. 1: enabled | 1 |  | R/W | 0 / 1
1402 | Functions: Hot water | Hot water no. 1: running | 1 |  | R | 0 / 1
1403 | Functions: Hot water | Hot water no. 1: temperature | x10 | °C | R
1404 | Functions: Hot water | Hot water no. 1: current setpoint | x10 | °C | R
1405 | Functions: Hot water | Hot water no. 1: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1406 | Functions: Hot water | Hot water no. 1: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1407 | Functions: Hot water | Hot water no. 1: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1410 | Functions: Hot water | Hot water no. 2: present | 1 |  | R | 0 / 1
1411 | Functions: Hot water | Hot water no. 2: enabled | 1 |  | R/W | 0 / 1
1412 | Functions: Hot water | Hot water no. 2: running | 1 |  | R | 0 / 1
1413 | Functions: Hot water | Hot water no. 2: temperature | x10 | °C | R
1414 | Functions: Hot water | Hot water no. 2: current setpoint | x10 | °C | R
1415 | Functions: Hot water | Hot water no. 2: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1416 | Functions: Hot water | Hot water no. 2: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1417 | Functions: Hot water | Hot water no. 2: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1420 | Functions: Hot water | Hot water no. 3: present | 1 |  | R | 0 / 1
1421 | Functions: Hot water | Hot water no. 3: enabled | 1 |  | R/W | 0 / 1
1422 | Functions: Hot water | Hot water no. 3: running | 1 |  | R | 0 / 1
1423 | Functions: Hot water | Hot water no. 3: temperature | x10 | °C | R
1424 | Functions: Hot water | Hot water no. 3: current setpoint | x10 | °C | R
1425 | Functions: Hot water | Hot water no. 3: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1426 | Functions: Hot water | Hot water no. 3: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1427 | Functions: Hot water | Hot water no. 3: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1430 | Functions: Hot water | Hot water no. 4: present | 1 |  | R | 0 / 1
1431 | Functions: Hot water | Hot water no. 4: enabled | 1 |  | R/W | 0 / 1
1432 | Functions: Hot water | Hot water no. 4: running | 1 |  | R | 0 / 1
1433 | Functions: Hot water | Hot water no. 4: temperature | x10 | °C | R
1434 | Functions: Hot water | Hot water no. 4: current setpoint | x10 | °C | R
1435 | Functions: Hot water | Hot water no. 4: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1436 | Functions: Hot water | Hot water no. 4: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1437 | Functions: Hot water | Hot water no. 4: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1440 | Functions: Hot water | Hot water no. 5: present | 1 |  | R | 0 / 1
1441 | Functions: Hot water | Hot water no. 5: enabled | 1 |  | R/W | 0 / 1
1442 | Functions: Hot water | Hot water no. 5: running | 1 |  | R | 0 / 1
1443 | Functions: Hot water | Hot water no. 5: temperature | x10 | °C | R
1444 | Functions: Hot water | Hot water no. 5: current setpoint | x10 | °C | R
1445 | Functions: Hot water | Hot water no. 5: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1446 | Functions: Hot water | Hot water no. 5: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1447 | Functions: Hot water | Hot water no. 5: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1450 | Functions: Hot water | Hot water no. 6: present | 1 |  | R | 0 / 1
1451 | Functions: Hot water | Hot water no. 6: enabled | 1 |  | R/W | 0 / 1
1452 | Functions: Hot water | Hot water no. 6: running | 1 |  | R | 0 / 1
1453 | Functions: Hot water | Hot water no. 6: temperature | x10 | °C | R
1454 | Functions: Hot water | Hot water no. 6: current setpoint | x10 | °C | R
1455 | Functions: Hot water | Hot water no. 6: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1456 | Functions: Hot water | Hot water no. 6: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1457 | Functions: Hot water | Hot water no. 6: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1460 | Functions: Hot water | Hot water no. 7: present | 1 |  | R | 0 / 1
1461 | Functions: Hot water | Hot water no. 7: enabled | 1 |  | R/W | 0 / 1
1462 | Functions: Hot water | Hot water no. 7: running | 1 |  | R | 0 / 1
1463 | Functions: Hot water | Hot water no. 7: temperature | x10 | °C | R
1464 | Functions: Hot water | Hot water no. 7: current setpoint | x10 | °C | R
1465 | Functions: Hot water | Hot water no. 7: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1466 | Functions: Hot water | Hot water no. 7: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1467 | Functions: Hot water | Hot water no. 7: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1470 | Functions: Hot water | Hot water no. 8: present | 1 |  | R | 0 / 1
1471 | Functions: Hot water | Hot water no. 8: enabled | 1 |  | R/W | 0 / 1
1472 | Functions: Hot water | Hot water no. 8: running | 1 |  | R | 0 / 1
1473 | Functions: Hot water | Hot water no. 8: temperature | x10 | °C | R
1474 | Functions: Hot water | Hot water no. 8: current setpoint | x10 | °C | R
1475 | Functions: Hot water | Hot water no. 8: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1476 | Functions: Hot water | Hot water no. 8: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1477 | Functions: Hot water | Hot water no. 8: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1480 | Functions: Hot water | Hot water no. 9: present | 1 |  | R | 0 / 1
1481 | Functions: Hot water | Hot water no. 9: enabled | 1 |  | R/W | 0 / 1
1482 | Functions: Hot water | Hot water no. 9: running | 1 |  | R | 0 / 1
1483 | Functions: Hot water | Hot water no. 9: temperature | x10 | °C | R
1484 | Functions: Hot water | Hot water no. 9: current setpoint | x10 | °C | R
1485 | Functions: Hot water | Hot water no. 9: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1486 | Functions: Hot water | Hot water no. 9: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1487 | Functions: Hot water | Hot water no. 9: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1490 | Functions: Hot water | Hot water no. 10: present | 1 |  | R | 0 / 1
1491 | Functions: Hot water | Hot water no. 10: enabled | 1 |  | R/W | 0 / 1
1492 | Functions: Hot water | Hot water no. 10: running | 1 |  | R | 0 / 1
1493 | Functions: Hot water | Hot water no. 10: temperature | x10 | °C | R
1494 | Functions: Hot water | Hot water no. 10: current setpoint | x10 | °C | R
1495 | Functions: Hot water | Hot water no. 10: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1496 | Functions: Hot water | Hot water no. 10: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1497 | Functions: Hot water | Hot water no. 10: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1500 | Functions: Swimming pool | Swimming pool no. 1: present | 1 |  | R | 0 / 1
1501 | Functions: Swimming pool | Swimming pool no. 1: enabled | 1 |  | R/W | 0 / 1
1502 | Functions: Swimming pool | Swimming pool no. 1: running | 1 |  | R | 0 / 1
1503 | Functions: Swimming pool | Swimming pool no. 1: temperature | x10 | °C | R
1504 | Functions: Swimming pool | Swimming pool no. 1: current setpoint | x10 | °C | R
1505 | Functions: Swimming pool | Swimming pool no. 1: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1506 | Functions: Swimming pool | Swimming pool no. 1: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1507 | Functions: Swimming pool | Swimming pool no. 1: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1510 | Functions: Swimming pool | Swimming pool no. 2: present | 1 |  | R | 0 / 1
1511 | Functions: Swimming pool | Swimming pool no. 2: enabled | 1 |  | R/W | 0 / 1
1512 | Functions: Swimming pool | Swimming pool no. 2: running | 1 |  | R | 0 / 1
1513 | Functions: Swimming pool | Swimming pool no. 2: temperature | x10 | °C | R
1514 | Functions: Swimming pool | Swimming pool no. 2: current setpoint | x10 | °C | R
1515 | Functions: Swimming pool | Swimming pool no. 2: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1516 | Functions: Swimming pool | Swimming pool no. 2: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1517 | Functions: Swimming pool | Swimming pool no. 2: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1520 | Functions: Swimming pool | Swimming pool no. 3: present | 1 |  | R | 0 / 1
1521 | Functions: Swimming pool | Swimming pool no. 3: enabled | 1 |  | R/W | 0 / 1
1522 | Functions: Swimming pool | Swimming pool no. 3: running | 1 |  | R | 0 / 1
1523 | Functions: Swimming pool | Swimming pool no. 3: temperature | x10 | °C | R
1524 | Functions: Swimming pool | Swimming pool no. 3: current setpoint | x10 | °C | R
1525 | Functions: Swimming pool | Swimming pool no. 3: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1526 | Functions: Swimming pool | Swimming pool no. 3: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1527 | Functions: Swimming pool | Swimming pool no. 3: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1530 | Functions: Swimming pool | Swimming pool no. 4: present | 1 |  | R | 0 / 1
1531 | Functions: Swimming pool | Swimming pool no. 4: enabled | 1 |  | R/W | 0 / 1
1532 | Functions: Swimming pool | Swimming pool no. 4: running | 1 |  | R | 0 / 1
1533 | Functions: Swimming pool | Swimming pool no. 4: temperature | x10 | °C | R
1534 | Functions: Swimming pool | Swimming pool no. 4: current setpoint | x10 | °C | R
1535 | Functions: Swimming pool | Swimming pool no. 4: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1536 | Functions: Swimming pool | Swimming pool no. 4: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1537 | Functions: Swimming pool | Swimming pool no. 4: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1540 | Functions: Swimming pool | Swimming pool no. 5: present | 1 |  | R | 0 / 1
1541 | Functions: Swimming pool | Swimming pool no. 5: enabled | 1 |  | R/W | 0 / 1
1542 | Functions: Swimming pool | Swimming pool no. 5: running | 1 |  | R | 0 / 1
1543 | Functions: Swimming pool | Swimming pool no. 5: temperature | x10 | °C | R
1544 | Functions: Swimming pool | Swimming pool no. 5: current setpoint | x10 | °C | R
1545 | Functions: Swimming pool | Swimming pool no. 5: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1546 | Functions: Swimming pool | Swimming pool no. 5: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1547 | Functions: Swimming pool | Swimming pool no. 5: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1550 | Functions: Swimming pool | Swimming pool no. 6: present | 1 |  | R | 0 / 1
1551 | Functions: Swimming pool | Swimming pool no. 6: enabled | 1 |  | R/W | 0 / 1
1552 | Functions: Swimming pool | Swimming pool no. 6: running | 1 |  | R | 0 / 1
1553 | Functions: Swimming pool | Swimming pool no. 6: temperature | x10 | °C | R
1554 | Functions: Swimming pool | Swimming pool no. 6: current setpoint | x10 | °C | R
1555 | Functions: Swimming pool | Swimming pool no. 6: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1556 | Functions: Swimming pool | Swimming pool no. 6: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1557 | Functions: Swimming pool | Swimming pool no. 6: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1560 | Functions: Swimming pool | Swimming pool no. 7: present | 1 |  | R | 0 / 1
1561 | Functions: Swimming pool | Swimming pool no. 7: enabled | 1 |  | R/W | 0 / 1
1562 | Functions: Swimming pool | Swimming pool no. 7: running | 1 |  | R | 0 / 1
1563 | Functions: Swimming pool | Swimming pool no. 7: temperature | x10 | °C | R
1564 | Functions: Swimming pool | Swimming pool no. 7: current setpoint | x10 | °C | R
1565 | Functions: Swimming pool | Swimming pool no. 7: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1566 | Functions: Swimming pool | Swimming pool no. 7: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1567 | Functions: Swimming pool | Swimming pool no. 7: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1570 | Functions: Swimming pool | Swimming pool no. 8: present | 1 |  | R | 0 / 1
1571 | Functions: Swimming pool | Swimming pool no. 8: enabled | 1 |  | R/W | 0 / 1
1572 | Functions: Swimming pool | Swimming pool no. 8: running | 1 |  | R | 0 / 1
1573 | Functions: Swimming pool | Swimming pool no. 8: temperature | x10 | °C | R
1574 | Functions: Swimming pool | Swimming pool no. 8: current setpoint | x10 | °C | R
1575 | Functions: Swimming pool | Swimming pool no. 8: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1576 | Functions: Swimming pool | Swimming pool no. 8: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1577 | Functions: Swimming pool | Swimming pool no. 8: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1580 | Functions: Swimming pool | Swimming pool no. 9: present | 1 |  | R | 0 / 1
1581 | Functions: Swimming pool | Swimming pool no. 9: enabled | 1 |  | R/W | 0 / 1
1582 | Functions: Swimming pool | Swimming pool no. 9: running | 1 |  | R | 0 / 1
1583 | Functions: Swimming pool | Swimming pool no. 9: temperature | x10 | °C | R
1584 | Functions: Swimming pool | Swimming pool no. 9: current setpoint | x10 | °C | R
1585 | Functions: Swimming pool | Swimming pool no. 9: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1586 | Functions: Swimming pool | Swimming pool no. 9: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1587 | Functions: Swimming pool | Swimming pool no. 9: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1590 | Functions: Swimming pool | Swimming pool no. 10: present | 1 |  | R | 0 / 1
1591 | Functions: Swimming pool | Swimming pool no. 10: enabled | 1 |  | R/W | 0 / 1
1592 | Functions: Swimming pool | Swimming pool no. 10: running | 1 |  | R | 0 / 1
1593 | Functions: Swimming pool | Swimming pool no. 10: temperature | x10 | °C | R
1594 | Functions: Swimming pool | Swimming pool no. 10: current setpoint | x10 | °C | R
1595 | Functions: Swimming pool | Swimming pool no. 10: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1596 | Functions: Swimming pool | Swimming pool no. 10: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1597 | Functions: Swimming pool | Swimming pool no. 10: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1600 | Functions: Support | Support no. 1: present | 1 |  | R | 0 / 1
1601 | Functions: Support | Support no. 1: enabled | 1 |  | R/W | 0 / 1
1602 | Functions: Support | Support no. 1: running | 1 |  | R | 0 / 1
1603 | Functions: Support | Support no. 1: temperature | x10 | °C | R
1604 | Functions: Support | Support no. 1: current setpoint | x10 | °C | R
1605 | Functions: Support | Support no. 1: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1606 | Functions: Support | Support no. 1: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1607 | Functions: Support | Support no. 1: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1610 | Functions: Support | Support no. 2: present | 1 |  | R | 0 / 1
1611 | Functions: Support | Support no. 2: enabled | 1 |  | R/W | 0 / 1
1612 | Functions: Support | Support no. 2: running | 1 |  | R | 0 / 1
1613 | Functions: Support | Support no. 2: temperature | x10 | °C | R
1614 | Functions: Support | Support no. 2: current setpoint | x10 | °C | R
1615 | Functions: Support | Support no. 2: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1616 | Functions: Support | Support no. 2: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1617 | Functions: Support | Support no. 2: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1620 | Functions: Support | Support no. 3: present | 1 |  | R | 0 / 1
1621 | Functions: Support | Support no. 3: enabled | 1 |  | R/W | 0 / 1
1622 | Functions: Support | Support no. 3: running | 1 |  | R | 0 / 1
1623 | Functions: Support | Support no. 3: temperature | x10 | °C | R
1624 | Functions: Support | Support no. 3: current setpoint | x10 | °C | R
1625 | Functions: Support | Support no. 3: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1626 | Functions: Support | Support no. 3: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1627 | Functions: Support | Support no. 3: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1630 | Functions: Support | Support no. 4: present | 1 |  | R | 0 / 1
1631 | Functions: Support | Support no. 4: enabled | 1 |  | R/W | 0 / 1
1632 | Functions: Support | Support no. 4: running | 1 |  | R | 0 / 1
1633 | Functions: Support | Support no. 4: temperature | x10 | °C | R
1634 | Functions: Support | Support no. 4: current setpoint | x10 | °C | R
1635 | Functions: Support | Support no. 4: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1636 | Functions: Support | Support no. 4: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1637 | Functions: Support | Support no. 4: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1640 | Functions: Support | Support no. 5: present | 1 |  | R | 0 / 1
1641 | Functions: Support | Support no. 5: enabled | 1 |  | R/W | 0 / 1
1642 | Functions: Support | Support no. 5: running | 1 |  | R | 0 / 1
1643 | Functions: Support | Support no. 5: temperature | x10 | °C | R
1644 | Functions: Support | Support no. 5: current setpoint | x10 | °C | R
1645 | Functions: Support | Support no. 5: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1646 | Functions: Support | Support no. 5: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1647 | Functions: Support | Support no. 5: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1650 | Functions: Support | Support no. 6: present | 1 |  | R | 0 / 1
1651 | Functions: Support | Support no. 6: enabled | 1 |  | R/W | 0 / 1
1652 | Functions: Support | Support no. 6: running | 1 |  | R | 0 / 1
1653 | Functions: Support | Support no. 6: temperature | x10 | °C | R
1654 | Functions: Support | Support no. 6: current setpoint | x10 | °C | R
1655 | Functions: Support | Support no. 6: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1656 | Functions: Support | Support no. 6: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1657 | Functions: Support | Support no. 6: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1660 | Functions: Support | Support no. 7: present | 1 |  | R | 0 / 1
1661 | Functions: Support | Support no. 7: enabled | 1 |  | R/W | 0 / 1
1662 | Functions: Support | Support no. 7: running | 1 |  | R | 0 / 1
1663 | Functions: Support | Support no. 7: temperature | x10 | °C | R
1664 | Functions: Support | Support no. 7: current setpoint | x10 | °C | R
1665 | Functions: Support | Support no. 7: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1666 | Functions: Support | Support no. 7: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1667 | Functions: Support | Support no. 7: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1670 | Functions: Support | Support no. 8: present | 1 |  | R | 0 / 1
1671 | Functions: Support | Support no. 8: enabled | 1 |  | R/W | 0 / 1
1672 | Functions: Support | Support no. 8: running | 1 |  | R | 0 / 1
1673 | Functions: Support | Support no. 8: temperature | x10 | °C | R
1674 | Functions: Support | Support no. 8: current setpoint | x10 | °C | R
1675 | Functions: Support | Support no. 8: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1676 | Functions: Support | Support no. 8: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1677 | Functions: Support | Support no. 8: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1680 | Functions: Support | Support no. 9: present | 1 |  | R | 0 / 1
1681 | Functions: Support | Support no. 9: enabled | 1 |  | R/W | 0 / 1
1682 | Functions: Support | Support no. 9: running | 1 |  | R | 0 / 1
1683 | Functions: Support | Support no. 9: temperature | x10 | °C | R
1684 | Functions: Support | Support no. 9: current setpoint | x10 | °C | R
1685 | Functions: Support | Support no. 9: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1686 | Functions: Support | Support no. 9: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1687 | Functions: Support | Support no. 9: setpoint 3 | x10 | °C | R/W | same limits as on the screen
1690 | Functions: Support | Support no. 10: present | 1 |  | R | 0 / 1
1691 | Functions: Support | Support no. 10: enabled | 1 |  | R/W | 0 / 1
1692 | Functions: Support | Support no. 10: running | 1 |  | R | 0 / 1
1693 | Functions: Support | Support no. 10: temperature | x10 | °C | R
1694 | Functions: Support | Support no. 10: current setpoint | x10 | °C | R
1695 | Functions: Support | Support no. 10: setpoint 1 | x10 | °C | R/W | same limits as on the screen
1696 | Functions: Support | Support no. 10: setpoint 2 | x10 | °C | R/W | same limits as on the screen
1697 | Functions: Support | Support no. 10: setpoint 3 | x10 | °C | R/W | same limits as on the screen
3000 | Electricity meters | Electricity meter no. 1: present | 1 |  | R | 0 / 1
3001 | Electricity meters | Electricity meter no. 1: power | x100 | kW | R | 32767 if the power is not measured
3002 | Electricity meters | Electricity meter no. 1: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3003 | Electricity meters | Electricity meter no. 1: energy index, low word | 1 |  | R
3004 | Electricity meters | Electricity meter no. 1: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3005 | Electricity meters | Electricity meter no. 2: present | 1 |  | R | 0 / 1
3006 | Electricity meters | Electricity meter no. 2: power | x100 | kW | R | 32767 if the power is not measured
3007 | Electricity meters | Electricity meter no. 2: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3008 | Electricity meters | Electricity meter no. 2: energy index, low word | 1 |  | R
3009 | Electricity meters | Electricity meter no. 2: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3010 | Electricity meters | Electricity meter no. 3: present | 1 |  | R | 0 / 1
3011 | Electricity meters | Electricity meter no. 3: power | x100 | kW | R | 32767 if the power is not measured
3012 | Electricity meters | Electricity meter no. 3: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3013 | Electricity meters | Electricity meter no. 3: energy index, low word | 1 |  | R
3014 | Electricity meters | Electricity meter no. 3: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3015 | Electricity meters | Electricity meter no. 4: present | 1 |  | R | 0 / 1
3016 | Electricity meters | Electricity meter no. 4: power | x100 | kW | R | 32767 if the power is not measured
3017 | Electricity meters | Electricity meter no. 4: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3018 | Electricity meters | Electricity meter no. 4: energy index, low word | 1 |  | R
3019 | Electricity meters | Electricity meter no. 4: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3020 | Electricity meters | Electricity meter no. 5: present | 1 |  | R | 0 / 1
3021 | Electricity meters | Electricity meter no. 5: power | x100 | kW | R | 32767 if the power is not measured
3022 | Electricity meters | Electricity meter no. 5: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3023 | Electricity meters | Electricity meter no. 5: energy index, low word | 1 |  | R
3024 | Electricity meters | Electricity meter no. 5: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3025 | Electricity meters | Electricity meter no. 6: present | 1 |  | R | 0 / 1
3026 | Electricity meters | Electricity meter no. 6: power | x100 | kW | R | 32767 if the power is not measured
3027 | Electricity meters | Electricity meter no. 6: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3028 | Electricity meters | Electricity meter no. 6: energy index, low word | 1 |  | R
3029 | Electricity meters | Electricity meter no. 6: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3030 | Electricity meters | Electricity meter no. 7: present | 1 |  | R | 0 / 1
3031 | Electricity meters | Electricity meter no. 7: power | x100 | kW | R | 32767 if the power is not measured
3032 | Electricity meters | Electricity meter no. 7: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3033 | Electricity meters | Electricity meter no. 7: energy index, low word | 1 |  | R
3034 | Electricity meters | Electricity meter no. 7: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3035 | Electricity meters | Electricity meter no. 8: present | 1 |  | R | 0 / 1
3036 | Electricity meters | Electricity meter no. 8: power | x100 | kW | R | 32767 if the power is not measured
3037 | Electricity meters | Electricity meter no. 8: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3038 | Electricity meters | Electricity meter no. 8: energy index, low word | 1 |  | R
3039 | Electricity meters | Electricity meter no. 8: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3040 | Electricity meters | Electricity meter no. 9: present | 1 |  | R | 0 / 1
3041 | Electricity meters | Electricity meter no. 9: power | x100 | kW | R | 32767 if the power is not measured
3042 | Electricity meters | Electricity meter no. 9: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3043 | Electricity meters | Electricity meter no. 9: energy index, low word | 1 |  | R
3044 | Electricity meters | Electricity meter no. 9: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3045 | Electricity meters | Electricity meter no. 10: present | 1 |  | R | 0 / 1
3046 | Electricity meters | Electricity meter no. 10: power | x100 | kW | R | 32767 if the power is not measured
3047 | Electricity meters | Electricity meter no. 10: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3048 | Electricity meters | Electricity meter no. 10: energy index, low word | 1 |  | R
3049 | Electricity meters | Electricity meter no. 10: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3100 | Heat meters | Heat meter no. 1: present | 1 |  | R | 0 / 1
3101 | Heat meters | Heat meter no. 1: power | x100 | kW | R | 32767 if the power is not measured
3102 | Heat meters | Heat meter no. 1: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3103 | Heat meters | Heat meter no. 1: energy index, low word | 1 |  | R
3104 | Heat meters | Heat meter no. 1: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3105 | Heat meters | Heat meter no. 2: present | 1 |  | R | 0 / 1
3106 | Heat meters | Heat meter no. 2: power | x100 | kW | R | 32767 if the power is not measured
3107 | Heat meters | Heat meter no. 2: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3108 | Heat meters | Heat meter no. 2: energy index, low word | 1 |  | R
3109 | Heat meters | Heat meter no. 2: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3110 | Heat meters | Heat meter no. 3: present | 1 |  | R | 0 / 1
3111 | Heat meters | Heat meter no. 3: power | x100 | kW | R | 32767 if the power is not measured
3112 | Heat meters | Heat meter no. 3: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3113 | Heat meters | Heat meter no. 3: energy index, low word | 1 |  | R
3114 | Heat meters | Heat meter no. 3: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3115 | Heat meters | Heat meter no. 4: present | 1 |  | R | 0 / 1
3116 | Heat meters | Heat meter no. 4: power | x100 | kW | R | 32767 if the power is not measured
3117 | Heat meters | Heat meter no. 4: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3118 | Heat meters | Heat meter no. 4: energy index, low word | 1 |  | R
3119 | Heat meters | Heat meter no. 4: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3120 | Heat meters | Heat meter no. 5: present | 1 |  | R | 0 / 1
3121 | Heat meters | Heat meter no. 5: power | x100 | kW | R | 32767 if the power is not measured
3122 | Heat meters | Heat meter no. 5: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3123 | Heat meters | Heat meter no. 5: energy index, low word | 1 |  | R
3124 | Heat meters | Heat meter no. 5: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3125 | Heat meters | Heat meter no. 6: present | 1 |  | R | 0 / 1
3126 | Heat meters | Heat meter no. 6: power | x100 | kW | R | 32767 if the power is not measured
3127 | Heat meters | Heat meter no. 6: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3128 | Heat meters | Heat meter no. 6: energy index, low word | 1 |  | R
3129 | Heat meters | Heat meter no. 6: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3130 | Heat meters | Heat meter no. 7: present | 1 |  | R | 0 / 1
3131 | Heat meters | Heat meter no. 7: power | x100 | kW | R | 32767 if the power is not measured
3132 | Heat meters | Heat meter no. 7: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3133 | Heat meters | Heat meter no. 7: energy index, low word | 1 |  | R
3134 | Heat meters | Heat meter no. 7: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3135 | Heat meters | Heat meter no. 8: present | 1 |  | R | 0 / 1
3136 | Heat meters | Heat meter no. 8: power | x100 | kW | R | 32767 if the power is not measured
3137 | Heat meters | Heat meter no. 8: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3138 | Heat meters | Heat meter no. 8: energy index, low word | 1 |  | R
3139 | Heat meters | Heat meter no. 8: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3140 | Heat meters | Heat meter no. 9: present | 1 |  | R | 0 / 1
3141 | Heat meters | Heat meter no. 9: power | x100 | kW | R | 32767 if the power is not measured
3142 | Heat meters | Heat meter no. 9: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3143 | Heat meters | Heat meter no. 9: energy index, low word | 1 |  | R
3144 | Heat meters | Heat meter no. 9: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
3145 | Heat meters | Heat meter no. 10: present | 1 |  | R | 0 / 1
3146 | Heat meters | Heat meter no. 10: power | x100 | kW | R | 32767 if the power is not measured
3147 | Heat meters | Heat meter no. 10: energy index, high word | 1 |  | R | index = (high word x 65536 + low word) / 10 kWh, unsigned
3148 | Heat meters | Heat meter no. 10: energy index, low word | 1 |  | R
3149 | Heat meters | Heat meter no. 10: state | 1 |  | R | 0 valid measurement, 1 disabled, 2 not set up or not connected, 3 faulty
10000-11500 | Inputs | Inputs: 10000 + line of the inputs table | x10 |  | R | 32767: not connected or faulty
20000-21500 | Outputs | Outputs: 20000 + line of the outputs table | 1 |  | R | 32767: not connected

## Commands
Allowed commands (Modbus functions 6 and 16)
Not allowed by default: tablet Internet screen, installer level, BMS enabled and "BMS commands allowed". An authorised IP address can be set. Each accepted command is written to the log.
Register | Command | Value written
101 | Heat pump enabled / disabled | 0 or 1
130 | Unblock the heat pump | 1 (any other value refused)
block + 1 | Function enabled / disabled | 0 or 1
block + 5 / + 6 / + 7 | Setpoint 1 / 2 / 3 of the function | setpoint x 10 (21.5 ° → 215), within the limits set on the tablet
Function block = 1000 + rank x 100 + (number - 1) x 10
Rank | Function | Blocks no. 1 to 9
0 | Hot room | 1000, 1010, 1020, 1030, 1040, 1050, 1060, 1070, 1080
1 | Cold room | 1100, 1110, 1120, 1130, 1140, 1150, 1160, 1170, 1180
2 | Hot tank | 1200, 1210, 1220, 1230, 1240, 1250, 1260, 1270, 1280
3 | Cold tank | 1300, 1310, 1320, 1330, 1340, 1350, 1360, 1370, 1380
4 | Hot water | 1400, 1410, 1420, 1430, 1440, 1450, 1460, 1470, 1480
5 | Swimming pool | 1500, 1510, 1520, 1530, 1540, 1550, 1560, 1570, 1580
6 | Support | 1600, 1610, 1620, 1630, 1640, 1650, 1660, 1670, 1680
Examples
Setpoint 1 of hot room no. 1 to 21 °: write 210 to register 1005
Disable hot water no. 1: write 0 to register 1401
Unblock the heat pump: write 1 to register 130

## Refusal codes
Answers when a command is refused (Modbus exceptions)
Code | Meaning
1 | Commands not allowed, client not authorised, or Modbus function not supported
2 | Register not writable, function missing, or address outside the map
3 | Value refused (out of limits, wrong number of registers, 130 other than 1)
4 | Tablet error
6 | Tablet busy: try again
Function 16: registers are applied one by one; if one is refused, the previous ones remain applied.

## Connection
Connection
Item | Value
Protocol | Modbus TCP, on the tablet's local network (Wi-Fi or Ethernet)
Port | 5020 by default, adjustable from 1024 to 65535 (502 not available)
Address | synapsus-<serial number>.local, or the tablet's IP address (plan a fixed or reserved IP)
Unit identifier | Any
Read | Functions 3 and 4 (same map), 125 registers at most per request
Write | Functions 6 and 16 if commands are allowed, 20 registers at most per request
Clients | 8 simultaneous connections at most; a connection silent for 2 minutes is closed
Refresh | Every 2 seconds; life counter (register 3) +1 per second
Stability | Areas 0 to 3149 stable from one version to the next; 10000 and 20000 depend on the wiring (troubleshooting)
Security | Neither password nor encryption: commands only on a controlled network, with the authorised IP address